## Slide 1
Enhancing Level of Service through risk-based asset management
Greg Norby, P.E.
General Manager
Vivian Housen, P.E.
Principal, VWHA
Northern California Pipe User’s Group
February 20, 2014

## Slide 2: Ross Valley Service Area
55,000 customers (~15,000 connections)
Average dry weather flow: 5 mgd
Peak wet weather flow: 55 mgd
194 miles of gravity sewers
8.4 miles of force mains
19 pump stations

## Slide 3: The district has many challenges
High Rainfall
Aging Infrastructure & Deferred Maintenance
Sensitive Environment
Funding and Rate Setting

## Slide 4: In addition, in May 2013 The district received a Cease and Desist Order
Required District to complete all historical capital improvements within 5 years
Price tag: > $100M
Fiscally infeasible
Did not promote asset management
Would have turned the entire community into a construction zone

## Slide 5: The RWQCB Agreed to an Infrastructure Asset Management Plan
Prioritized Needs to Rapidly Address Risk
Justified Fewer Projects Over a Longer Period
Gained Valuable Time Needed to Fine-Tune the Most Costly Projects
Builds In Flexibility to Adjust Priorities Based on Continued Assessments

## Slide 6: The cease and desist Order demanded Accelerated pipeline rehabilitation
The District Met This Challenge Using A Numerical Risk Management Tool

## Slide 7
ASSET MANAGEMENT IS A FLUID AND PERPETUAL PROCESS
Understand your system and Level of Service objectives
Be diligent about extending useful life
Take action when an asset must be replaced to sustain the desired Level of Service

## Slide 8: Using an asset management approach, Ross Valley gained control over the CIP
Miles of Pipe
1980
2025
2013
2040
Approximate replacement schedule based on a 75-year service life
Capital Spending Using an Asset Management Approach
Capital Spending Using a Reactive Approach

## Slide 9
The risk model is designed to produce rapid results in SSO reduction
Reliability Objectives
Time
Sewer
Management
Objectives
Risk Reduction Using the Risk Management Tool
Risk Reduction Using “Business as Usual”

## Slide 10
How the risk management tool works
Likelihood of Failure (from InfoNet CMMS)
Material (Techite)
Structural Condition
O&M Condition
Located in Bay Mud
Located in Landslide Zone
Capacity/SSOs
Maintenance Needs
Consequence of Failure (GIS Data)
Near Waterway
Near School, Park
Crosses Major Roadway
Serves Large Area
Risk Score for Every Pipe Segment

## Slide 11: Level of Service Objectives form the basis for the risk model decision tree
Reliability – Make Sure the System Works
Environmental Protection – Protect Public Health and our Waterways
Community Impact – Keep the Sewers Invisible
Cost – Provide High Level of Service at the Lowest Sustainable Cost to the Community

## Slide 12: Infonet cmms provides critical information in the decision to renew or replace Pipelines
Preventive Maintenance Program
CMMS*
Repair or Replace
* Computerized Maintenance
Management System
Real-Time Data
Managed Risk

## Slide 13: Raw cCTV data for half the system painted a serious picture
Red lines indicate at least one NASSCO PACP Structural Grade 4 or 5 Defect

## Slide 14
Key question – do all of these defects need to be fixed now?
Answer is no …
GIS tools define the Consequence of Failure. Proximity to a waterway was the primary factor affecting replacement priorities.

## Slide 15
Critical Arterial Roadways are differentiated in the model as Primary and Secondary
If a pipe break would impact on a major transportation corridor, the pipe was elevated in criticality.

## Slide 16
Other factors defined likelihood and consequence of failure
Techite
NASSCO PACP
Maintenance History
Geologic Features
Proximity to Parks or Schools
Area Served

## Slide 17
Calibration of the risk model prevented overlapping criteria from skewing results
Landslide Zone
Parks
Bay Mud
Schools
Each criteria carried an individual weight and score. Overlapping criteria were either weighted or grouped to control total criticality.

## Slide 18: Risk Tool Show that 10% of the system’s pipes contain the highest risk
Chart: 
 | 64211 | 30419 | 11609 | 58008 | 352708 | 458432
Highest Risk Pipes Have PACP Str Gr5 or Techite plus..
7%
3%
High Consequence
Moderate Consequence
Other Pipes Require
Re-inspection and Reassessment
6%
Many Pipes Require No Corrective Action
36%
Inspection in
Process

## Slide 19
The Risk management Results painted a more strategic picture
Raw Scores
Risk Assessment

## Slide 20
The Risk Model Also shows Us where the next group of issues may occur
These pipes have not failed, but are showing signs of aging and are in high consequence locations
Monitor closely during regular O&M activities

## Slide 21
To focus the program further, the program used a surgical approach to repairs
1 or 2 Point Repairs
Pipe Replacement

## Slide 22
Linear asset management was one component of a multi-faceted program
Pump Stations Were Reviewed for:
Firm Capacity
Outage Reliability
Useful Life
RWQCB Agreed to Defer Costly Force Main Replacements Until Field Assessments are Completed
O&M Activities Inform and Support Program Changes

## Slide 23: RESULTS!!
40 percent reduction in capital funding requirement
Highest priority items addressed first for early results
Regional Board reviewed and had minor comments – extended timeline and flexible approach were approved
RVSD is now well positioned for lifecycle asset management

## Slide 24: Top five things to take away from this Presentation
Good data is critical to successful decisionmaking
About ten percent of the system presents the majority of risk
By addressing these ten percent, a high Level of Service can be achieved
Replacement costs can be controlled through a surgical approach to pipeline repairs
This approach has been accepted by the Regional Board

## Slide 25
Enhancing Level of Service through risk-based asset management
Greg Norby, P.E.
gnorby@rvsd.org
Vivian Housen, P.E.
vhousen@housenassociates.com
Northern California Pipe User’s Group
February 20, 2014